| Certificate number | ES-R-12-001 | Revision | Rev. 00 |
| --- | --- | --- | --- |
| Client | DEMO – Sample Process Plant (not a real client) | Site | Demo Utilities Area |
| Tag number | PSV-101A | Description | Steam drum safety valve A |
| Manufacturer | Demo Valves | Model | SV-3 |
| Serial number | DV-1101 | Date of test | 09 Oct 2026 |

1. VALVE DATA

| Valve type | Conventional spring | Protected equipment | B-101 steam drum |
| --- | --- | --- | --- |
| Inlet size | 3 in | Outlet size | 4 in |
| Orifice | J | Service | Steam |

2. TEST RESULTS

| Parameter | Value | Result |
| --- | --- | --- |
| Set pressure | 43 bar |  |
| Tolerance | ± 0.689 bar | ASME I |
| Cold differential test pressure | 43 bar |  |
| As-found pop pressure | 44.6 bar | Outside tolerance |
| As-left set pressure | 43.1 bar | Within tolerance |
| Reseat pressure | 40.5 bar |  |
| Seat tightness (API 527) |  | Pass |
| Test medium | Air |  |
| Test bench / gauge | ES-TB-01 / G-114 (cal. due 2027-03) |  |

3. PARTS CONDITION

| Part | Condition found | Action taken |
| --- | --- | --- |
| Disc | Light wire drawing | Lapped |
| Seat | Light wire drawing | Lapped |
| Spring | Good | None |

Final result: ACCEPTED. We certify that the valve was tested and set at 43.1 bar, found within the required tolerance, and sealed.

| Valid until / next test due | 09 Oct 2027 |
| --- | --- |

| Tested / examined by | Witnessed by | Issued by |
| --- | --- | --- |
| Demo Inspector Senior Inspector · Cert. API 510 #00000 Date: 09 Oct 2026 | Demo Plant Engineer Date: | Demo Office Lead Date: 10 Oct 2026 |